## Sheet2
Declaration of Performance
Unique Identifer: |  | FrameFit, Bringing Life Back To Fire Doors
Country of Manufacture/Origin: |  | United Kingdom
Intended Use: |  | FrameFit has been designed and tested to remediate gaps all round FD30 and FD60 fire doors. It can remediate gaps on the hinge side, latch side, door head, door base and meeting stiles, threshold. FrameFit can be used individually on one edge or on all edges of a door as required.
Components/References | HE | HE/44mm and HE/54mm = High Expansion intumescent (x20 expansion) which includes a cold smoke seal tested to BS EN 1634-3:2004. The HE is used to replace existing intumescent that is in the door frames of FD30 and FD60 doors.
| LM | LM/44mm and LM/54mm = Low Modulus fire retardent material used as a 'bulk' gap reducer. It is available in 1.5mm, 3mm and 5mm thicknesses and can be adhered together to close larger gaps and can be used with FD30 and FD60 doors.
| BDS | BDS30 and BDS60 = FrameFit Bottom Door Seal that can be packed with the required amount of FrameFit LM and used to remediate gaps to the door base. The BDS 30 is used for FD30 doors and the BDS60 is used for FD60 doors.
| MES | MES30 and MES60 - MES Meeting Edge Seal includes an inner layer of 1.5mm high expansion intumescent and can be packed with the LM variant of FrameFit to close gaps between double doors.
| TS | TS = FrameFit Threshold seal can be packed with the LM variant of FrameFit to close gaps to the base of the door and is fixed to the floor, not the door. This addresses issues with uneven/unlevel floors.
| FFHP | FrameFit intumescent Hinge Pads: FFHP/R for radius hinges, FFHP/S for square hinge.
| FFNL | FFNL = Intumescent Night Latch Lock kit. |  | Lock spindle bore 32mm
| FFPP | FFPP = Perko Closer intumescent remedial kit
Regulation Standards |  | FrameFit has been tested to conform to the following Fire Door testing standards BS476pt 22:1987 & BSEN 1634-1:2014+A1 2018.
Door cores tested |  | FD30 = PAS24, GDC, Cross Laminated Timber (CLT), Strebord, Stiled & Railed, Solid Core Softwood, Premdor FD60 = GDC Single and Double
Frame materials tested |  | MDF, Hardwood and Softwood
Declared Performance
Test Standard Ref No. | UK Test and Certification Centre Test Ref No. | FrameFit component | Door Manufacturer | Single (S) or Double (D) leaf | Leaf Size | Core Material | Frame Material | Perimeter Gaps |  |  |  | Results (mins)
[8 empty] | Hinge | Latch | Head | Foot | Integrity | Insulation
Test 1 - Test Standard BS476 pt22:1987 | 20220311-005314 | Framefit LM, HE and BDS | Halspan FD30 Prima | S | 2040 x 932 x 44 | GDC | MDF | 3 | 15 | 12 | 25 | 41 | 41
|  |  | Halspan FD60 Prima | S | 2040 x 932 x 54 | GDC | Hardwood | 3 | 15 | 12 | 25 | 63 | 63
Test 2 - Test Standard BSEN1634-1:2014+A1 2018 | 20220428-04633B | FrameFit LM, HE and BDS | Vicaima Stiled and Railed FD30 | S | 926 x 2040 x 44 | Solid Core | Softwood | 3 | 15 | 12 | 25 | 34 | 34
Test 3 - Test Standard BSEN1634-1:2014+A1 2018 | 20220624-105409 | Framefit LM, HE and BDS | Halspan FD30 IT | S | 2040 x 930 x 44 | Cross laminated timber lamels | MDF | 3 | 9 | 10 | 14 | 38 | 38
|  |  | B Halspan FD30 Prima PAS 24 | S | 2040 x 930 x 44 | GDC | Hardwood | 3 | 9 | 9 | 15 to 25 | 55 | 55
| 20220817-105713 | Framefit LM, HE and BDS | Strebord FD30 | S | 2040 x 930 x 44 | GDC | Softwood | 3 | 5 | 3 | 17 | 31 | 31
Test 4 - Test Standard |  | Meeting Edge Seal
BSEN1634-1:2014+A1 2018 |  | (FrameFit MES) | Halspan FD60 Prima | D | 2040 x 500 x 54 x 2 | GDC | Softwood | 3 | 15 | 6 | 13 | 38 | 38
Test 5 - Test Standard | 20221031-005814 | Framefit LM and HE | Falcon Panel Products FD60 | S | 2040 x 930 x 54 | GDC | Hardwood | 3 | 3 | 6 | N/A | 66 | 66
BSEN1634-1:2014+A1 2018 | 20221031-005814 | FrameFit Threshold Seal, HE & LM | Falcon Panel Products FD60 | S | 2040 x 930 x 54 | GDC | Hardwood | 3 | 3 | 6 | 20 | 66 | 66
Test 6 - Test Standard BSEN1634-1:2014+A1 2018 | 20230223-002310 | Threshold, Framefit LM and HE | Halspan FD30 Prima | S | 2040 x 928 x 44 | Multi-layered Particle Board | Softwood | 3 | 5 | 5 | N/A | 30 | 30
Test 7 - Test Standard | 20231206-004709 | Threshold, BDS, Hinge Pads, Yale Night Latch Intumescent lock kit, HE & LM | Premdor | S | 2040 x 926 x 44 | Solid Core Chipboard | Softwood | 3 | 8 | 3 | 30 | 31 | 31
BS476 pt22:1987 | 20231206-004709 | Threshold, Meeting Edge Seal (FrameFit MES), HE & LM | Halspan FD60 Prima | D | 2040 x 941 x 54 | GDC | Sapele | 3 | 15 | 6 | 18 | 66 | 66
Test 8 - Test Standard | 20241101-001311 | FrameFit HE44 (partial) | JELD_WEN UK | S | 2036 x 926 x 44 |  | Softwood | 3 | N/A |  | N/A | 33 | 33
BS476 pt22:1987 | 20241101-001311 | ERA Night Latch Intumescent lock kit, Perko Plug | CF160 | S | 2036 x 926 x 44 |  | Softwood | 3 | N/A | N/A | N/A | 33 | 33