## Sheet1
Unique Identifer: |  | Speedcutter - Fire and Smoke protection for partiton walling
Country of Manufacture/Origin: |  | United Kingdom
Intended Use: |  | Speedcutter has been designed and tested to protect service penetrations in plasterboard walls.
Product References | SC35
SC50
SC80
SC117
Regulation Standards | Speedcutter has been tested to conform to the following service penetration testing standards BS EN 1366-3:2021 + A12024.
Speedcutter has been tested to conform to the following air leakage testing standards BS EN 1634-3:2004.
Penetration materials tested | MT Supertube - P-EX Pipe - PB Pipe - Cat A & Cat 6a Data Cables - Twin & Earth Wiring Cable - Blank
Integrity & insulation | 2025-09-29 | Test Specimen | Speedcutter | Penetration | Size |  | Results |  | Integrity &
Test No 20250826-001017 | Report No | Reference | Reference | Material | mm |  | Integrity | Insulation | Insulation Rating
BS EN 1366-3:2021 + A12024 | 20250826-001017 | C |  | MT Supertube | 25mm
|  |  | SC35 | LSOH (polyethylene) 3-layer conduit |  |  | 72 | 72 | EI60
BS EN 1366-3:2021 + A12024 | 20250826-001017 | D |  | P-EX Pipe | 28mm
|  |  | SC35 | Polyethylene |  |  | 72 | 52 | EI52
BS EN 1366-3:2021 + A12024 | 20250826-001017 | E |  | PB Pipe
|  |  | SC35 | Polybutylene | 10mm |  | 72 | 72 | EI60
BS EN 1366-3:2021 + A12024 | 20250826-001017 | F |  | P-EX Pipe
|  |  | SC35 | Polyethylene | 15mm |  | 72 | 72 | EI60
BS EN 1366-3:2021 + A12024 | 20250826-001017 | G |  | Blank
|  |  | SC117 |  | N/A |  | 72 | 72 | EI60
BS EN 1366-3:2021 + A12024 | 20250826-001017 | H |  | Cat6 & Cat6A | Bunch
|  |  | SC80 | Data Cable | 24No |  | 72 | 72 | EI60
BS EN 1366-3:2021 + A12024 | 20250826-001017 | I |  | Twin Earth | Bunch
|  |  | SC35 | Flat PVC Wiring Cable | 5No |  | 72 | 72 | EI60
BS EN 1366-3:2021 + A12024 | 20250826-001017 | J |  | Twin Earth
|  |  | SC35 | Flat PVC Wiring Cable | 1No |  | 72 | 72 | EI60
Air Leakage | 29//09/2025 | Untaped | Face exposed | Speedcutter Reference | Size | Total | Leakage | Linear | Leakage
Test No TR20250826-001117 | Report No | Taped | to pressure | Penetration Material | mm | 10Pa | 25Pa | 10Pa | 25Pa
BS EN 1634-3:2004 | 20250826-001117 | Untaped | Side A | SC35 - Blank | Test 1 | 2.4 | 4.08 | 0.48 | 0,81
|  |  | Side B | SC35 - Blank | Test 2 | 2.16 | 4.07 | 0.43 | 0.81
BS EN 1634-3:2004 | 20250826-001117 | Untaped | Side A | SC35 - Blank | Test 1 | 2.2 | 4.41 | 0.44 | 0.88
|  |  | Side B | SC35 - Blank | Test 2 | 4.46 | 3.9 | 0.89 | 0.78
BS EN 1634-3:2004 | 20250826-001117 | Door untaped SC80 taped | Side A | SC80 - Twin Earth | Test 1 | 3.86 | 6.71 | 0.77 | 1.33
|  |  | Side B | Flat PVC Wiring Cable | Test 2 | 3.88 | 7.09 | 0.77 | 1.14